## Slide 1: A novel filtration configuration for targeted humic acid removal from drinking water
Maebh A. Grace, Mark G. Healy, Eoghan Clifford

## Slide 2: Overview
Introduction
Why Natural Organic Matter?
Materials and Methods
Filter construction
Results and conclusion
Performance results and conclusions
Our solution

## Slide 3: Introduction
NOM in drinking water
Disinfectant
Disinfection by-product formation
Measured as organic carbon
Trihalomethanes
Haloacetic acids
Toxic
Carcinogenic
Chlorine
Ozone

## Slide 4: Introduction
Why target NOM?
Plentiful NOM sources
Highest TTHM recorded:
245 µg L-1
Retrofitting not redesigning
10 % Total Trihalomethane non-compliance in Ireland
Max allowable THM (mg L-1)
US: 80
Europe: 100
Current solutions are expensive and unsustainable
Reuse of waste material for a cost-effective and sustainable solution
Redesign the traditional sand filter using novel media

## Slide 5: Materials and Methods
Media Classification – adsorption isotherms for DOC
Media | Isotherm | R2 | Qmax (µg g-1) | 1/n | K
Sand | Desorption |  |  |  | 
Zeolite | Langmuir | 0.71 | 37 |  | 
Fly ash | Freundlich | 0.73 |  | 1.17 | 0.262
GAC | Langmuir | 0.42 | 327 |  | 
Bayer residue | Freundlich | 0.83 |  | 0.68 | 0.019

## Slide 6: Materials and Methods
Filter construction and operation
Control
Config 1
Config 2
Flyash
GAC
Zeolite
Sand
Bayer
Residue
Zeolite
Sand
Sand
1 m of media as per EPA guidelines
2 loading regimes
  Constant and intermittent
Dosed with a synthetic mix
  Humic acid as TOC source

## Slide 7: Materials and Methods
Humic acid as TOC source
  Representative of DOC from peatland areas
    Relevant for Irish water treatment facilities
  Laboratory grade
  Process to extract and dispose of insoluble fraction
Add to water and mix for 25 min
Centrifuge at 1000 RPM for 30 min
Filter through 0.45 µm filter

## Slide 8: Results
Loading Regime |  | Average concs mg DOC L-1 | % DOC Removal
Continuous | Influent Concentration | 5.8 ± 2.2 | 
 | Effluent Concentration |  | 
 | Control | 4.2 ± 1.9 | 27.6 ± 3.3
 | Config 1 | 3.7 ± 1.8 | 36.2 ± 10.9
 | Config 2 | 1.7 ± 1.6 | 58.8 ± 4.8
Intermittent | Influent Concentration | 6.0 ± 1.7 | 
 | Effluent Concentration |  | 
 | Control | 4.5 ± 1.8 | 25 ± 2.5
 | Config 1 | 4.0 ± 1.8 | 33.3 ± 4.8
 | Config 2 | 2.3 ± 1.6 | 61.6 ± 10
Config 1:
Bayer Residue
Zeolite
Sand
Config 2:
Fly ash
GAC
Zeolite
Sand

## Slide 9: Results
Continuous
Intermittent
Chart: Control
| 40.909090909090907 | 36.36363636363636 | 49.494949494949502
0 | 0.33 | 0.66 | 1
45 | 0.33 | 0.66 | 1
90 | 0.33 | 0.66 | 1
Chart: Control
| 2.0833333333333397 | 26.562500000000011 | 31.770833333333343
 | 0.33 | 0.66 | 1
45 | 0.33 | 0.66 | 1
90 | 0.33 | 0.66 | 1
% DOC Removal
Depth from surface (m)

## Slide 10: Results
Continuous
Intermittent
% DOC Removal
Depth from surface (m)
Chart: Config 1
| 84.722222222222229 | 33.333333333333336 | 34.898647451796684
 | 0.33 | 0.66 | 1
0 | 0.33 | 0.66 | 1
45 | 0.33 | 0.66 | 1
Chart: Config 1
| 69.427083333333329 | 56.25 | 59.203980099502495
0 | 0.33 | 0.66 | 1
45 | 0.33 | 0.66 | 1
90 | 0.33 | 0.66 | 1
Config 1:
Bayer Residue
Zeolite
Sand

## Slide 11: Results
Continuous
Intermittent
% DOC Removal
Depth from surface (m)
Chart: Config 2
| 52 | 82 | 68 | 71.510604536988865
 | 0.25 | 0.5 | 0.75 | 1
 | 0.25 | 0.5 | 0.75 | 1
 | 0.25 | 0.5 | 0.75 | 1
Chart: Config 2
| 77.604166666666671 | 82.8125
0 | 0.25 | 1
45 | 0.25 | 1
90 | 0.25 | 1
Config 2:
Fly ash
GAC
Zeolite
Sand

## Slide 12: Discussion
Both configurations more effective than control
  Configuration 2 most effective
Clogging was observed across all filter configurations
  Humic acid mix: high suspended solids
  Approx. 200 mg L-1
DOC removal decreased over time
  Clogging of upper layers, DOC leaching
  and media saturation
Config 2:
Fly ash
GAC
Zeolite
Sand

## Slide 13: Clogging Issue
Chart: K/Kv
| 0.53977769824226507 | 0.32206911636045488 | 0.43809154537500994 | 0.66931122246082864 | 0.52454664757814351 | 0.4595363079615048 | 0.30358705161854771 | 0.14536109122723295 | 0.28748111031575596 | 0.42134931997136715 | 0.37246480553567163 | 0.49779288952517309 | 0.85510697526445556 | 0.56430446194225725 | 1
Control | 0.01 | 0.03 | 0.05 | 0.07 | 0.09 | 0.11 | 0.13 | 0.15 | 0.17 | 0.19 | 0.21 | 0.23 | 0.25 | 0.27 | 0.29
Chart: K/Kv
| 0.34446828072326086 | 0.32367466360724095 | 0.52858650866619006 | 0.32600799955994558 | 0.35069976504239453 | 0.48862904725607748 | 0.76946061906221264 | 0.77382305099130133 | 1
 | 0.01 | 0.03 | 0.05 | 0.07 | 0.09 | 0.11 | 0.13 | 0.15 | 0.17
Chart: K/Kv
| 0.40194861930216719 | 0.46317529549476311 | 0.63221407254128326 | 0.97353125289154607
 | 0.025 | 0.075 | 0.125 | 0.175
Clogging results for continuously loaded filters
  Constant head permeability test
  Falling head permeability test
Clogging of control extended further below surface
Clogging of config 1 and config 2 was very similar
K/Kv: Normalised hydraulic conductivity

## Slide 14: Outlook for technology adoption
DBP formation potential removed at filtration stage
  Plants can be retrofitted rather than redesigned
Media can become saturated
  Potentially mitigated by replacing the clogging layer
Media may need repositioning, given potential for clogging
Further work involves investigation of other contaminants and media combinations

## Slide 15: Conclusions
Alternative media may be used for NOM removal
  Bayer residue, fly ash, zeolite and GAC
Sustainable design, using locally available waste materials
Config 2 was most effective
  Clogging did occur
Both configs were more effective than a standard sand filter
A redesign will mitigate clogging, while maintaining a successful and sustainable technology
Config 2:
Fly ash
GAC
Zeolite
Sand

## Slide 16: Questions?
Thank you for your attention
Any Questions?